## Heatloss
************************* Notes on Use ********************************** For each room take a wall and fill the details of the construction in across the page, then move to the next row and fill in the next wall. The order in which the walls is filled in is not relevant. The floor and ceiling infromation only needs to be filled in on the floor and ceiling rows. Don't forget to fill in the delta T section for each wall, ceiling and floor on the far right. Use the Required Heat Output value to calculate (or check) required pipe spacings. I've used pipe with 10W/meter so the spacing between rows needs to be (Required Heat Output Value)/10. This will give the maximum pipe spacing in Metres. In reality most systems use 150 or 120 mm spacing unless the pipework is installed free hand. You need to make sure that your system has enough output to overcome the heat losses.
Room | Kitchen |  |  |  |  | Wall Construction (For Single Leaf Wall just fill in 'Outer Leaf' and 'Interior Finish' leave other columns blank
|  | Height | Width | Total Area | Windows & Doors | Outer Leaf (Including Surface Resistance) | Cavity | Inner Leaf | Wall Interior Finish (Including Surface Resistance) | Floor Type (Only fill in on the floor row) | Ceiling (Only fill in on the Ceiling row) | U value | U value | Room temp | Outside temp | ∆t | Heatloss
|  | [m] | [m] | [m^2] | (Select from drop down list) | (Select from drop down list) | (Select from drop down list) | (Select from drop down list) | (Select from drop down list) | (Select from drop down list) | (Select from drop down list) | [W/m^2.K] | [W/m^2.k] | [°C] | [°C] | [°C] | [W/hr]
| Wall 1 | 2.3 | 3.5 | 8.05 | None | Double Brick | None | None | Insualted plaster board (Gyproc Thermaline Super) 50 mm | None | None | 0.41373 | 0.41373 | 20 | -3 | 23 | 76.6017
| Windows/Doors | 0 | 0 | 0 | None | None | None | None | None | None | None | 4.9261 | 0 |  | 0 | 0 | 0
| Wall 2 | 2.3 | 3.65 | 8.395 | None | Double Brick | None | None | Insualted plaster board (Gyproc Thermaline Super) 50 mm | None | None | 0.41373 | 0.41373 | 20 | 15 | 5 | 17.3662
| Windows/Doors |  |  |  | None | None | None | None | None | None | None | 4.9261 | 0 |  |  |  | 0
| Wall 3 | 2.3 | 3.5 | 6.25 | None | Double Brick | None | None | Insualted plaster board (Gyproc Thermaline Super) 50 mm | None | None | 0.41373 | 0.41373 | 20 | -3 | 23 | 59.4734
| Windows/Doors | 1.8 | 1 | 1.8 | Single Glazed Window with K glass | None | None | None | None | None | None | 1.6331 | 1.6331 | 20 | -3 | 23 | 67.6103
| Wall 4 | 2.3 | 3.65 | 8.395 | None | Double Brick | None | None | Insualted plaster board (Gyproc Thermaline Super) 50 mm | None | None | 0.41373 | 0.41373 | 20 | 15 | 5 | 17.3662
| Windows/Doors |  |  |  | None | None | None | None | None | None | None | 4.9261 | 0 |  |  |  | 0
| Floor | 3.5 | 3.65 | 12.775 | None | None | None | None | None | Concrete (100mm) over Phenolic Board (100mm) | None | 0.28117 | 0.28117 | 20 | 10 | 10 | 35.9192
| Ceiling | 3.5 | 3.65 | 12.775 | None | None | None | None | None | None | Plaster Board With (100mm mineral wool and skim) | 0.33115 | 0.33115 | 20 | 20 | 0 | 0
[15 empty] | Total Heat loss |  | 274.3371 | W/hr
| Live floor area |  |  | 9.895
[14 empty] | Required heat output from UFH |  |  | 27.7248 | W/m^2
Room | Bathroom
|  | Height | Width | Total Area
|  | [m] | [m] | [m^2]
| Wall 1 | 2.4 | 1.55 | 2.295 | None | Double Brick | None | None | Insualted plaster board (Gyproc Thermaline Super) 50 mm | None | None | 0.41373 | 0.41373 | 22 | -3 | 25 | 23.7376
| Windows/Doors | 1.5 | 0.95 | 1.425 | Secondary Double Glazed (4mm Hard E Coat glass) | None | None | None | None | None | None | 1.3544 | 1.3544 | 22 | -3 | 25 | 48.2507
| Wall 2 | 2.4 | 2 | 3.375 | None | Concrete Block (Medium Weigth) | None | None | Plaster Board (13mm inc skim) | None | None | 2.1145 | 2.1145 | 22 | 20 | 2 | 14.2727
| Windows/Doors | 1.5 | 0.95 | 1.425 | None | None | None | None | None | None | None | 4.9261 | 0 | 22 | 20 | 2 | 0
| Wall 3 | 2.4 | 2 | 3.375 | None | Concrete Block (Medium Weigth) | None | None | Plaster Board (13mm inc skim) | None | None | 2.1145 | 2.1145 | 22 | 20 | 2 | 14.2727
| Windows/Doors | 1.5 | 0.95 | 1.425 | None | None | None | None | None | None | None | 4.9261 | 0 | 22 | 20 | 2 | 0
| Wall 4 | 2.4 | 2.2 | 5.28 | None | Double Brick | None | None | Insulated plaster Board (Gyproc Thermaline Basic) 22 mm | None | None | 1.2546 | 1.2546 | 22 | 15 | 7 | 46.3711
| Windows/Doors |  |  |  | None | None | None | None | None | None | None | 4.9261 | 0 | 22 | 15 | 7 | 0
| Floor | 2.2 | 2 | 4.4 | None | None | None | None | None | Concrete (100mm) over Phenolic Board (100mm) | None | 0.28117 | 0.28117 | 22 | 10 | 12 | 14.8457
| Ceiling | 2.2 | 2 | 4.4 | None | None | None | None | None | None | Plaster Board With (100mm mineral wool and skim) | 0.33115 | 0.33115 | 22 | 20 | 2 | 2.9141
[15 empty] | Total Heat loss |  | 164.6647 | W/hr
| Live floor area |  |  | 2.79
[14 empty] | Required heat output from UFH |  |  | 59.0196 | W/m^2
Note on B17: Quirk: The live floor area is the floor area which will be underfloor heated. UFH is not fitted under kitchen units, baths, shower trays or WC's so any area these cover needs to be subtracted from the room total floor area
Note on B34: Quirk: The live floor area is the floor area which will be underfloor heated. UFH is not fitted under kitchen units, baths, shower trays or WC's so any area these cover needs to be subtracted from the room total floor area
Note on E5: Quirk: This is the total area of the wall less the area of any window or door from the row below.
Note on E22: Quirk: This is the total area of the wall less the area of any window or door from the row below.
Note on M3: Quirk: These come from the data in Column H in the Lookups & Conductivity worksheet, these are combined U values and include the internal and external surface resistances (0.123 & 0.080 respectively but see the table on the Lookups worksheet for more values)
Note on P3: Quirk: Outside temp is assumed at -3C for external walls, 10C for cellar walls and floor in contact with the ground. Adjacent are assumed to be heated to a lower temperature of 15C

## Lookups & Conductivity
This worksheet contains the technical data to calculate the combined 'U' values used in the heat loss sheet
Construction Type Single Elements | Thickness | Conductivity | Thermal Resistance | U Value |  | Notes
Walls | [5 empty] | Two layers of brick, no cavity
None |  |  | 0
Double Brick | 0.205 | 0.84 | 0.24405 | 4.0976
Single Brick (Outer Leaf of Wall | 0.1 | 0.84 | 0.11905 | 8.4
Single Brick (Inner Leaf of Wall) | 0.1 | 0.62 | 0.16129 | 6.2
Concrete Block (Light weight) | 0.1 | 0.18 | 0.55556 | 1.8
Concrete Block (Medium Weigth) | 0.1 | 0.53 | 0.18868 | 5.3
Finishes
None |  |  | 0
Plaster Board (13mm inc skim) | 0.013 | 0.16 | 0.08125 | 12.3077
Insulated plaster Board (Gyproc Thermaline Basic) 22 mm |  |  | 0.35 | 2.8571
Insulated plaster board (Gyproc Thermaline Super) 40 mm |  |  | 1.49 | 0.67114
Insualted plaster board (Gyproc Thermaline Super) 50 mm |  |  | 1.97 | 0.50761
Insualted plaster board (Gyproc Thermaline Super) 60 mm |  |  | 2.56 | 0.39062
Windows_Doors | [5 empty] | No value here: Pilkington do not recommend the use of K glass in sigle glazed applications
None |  |  | 0 |  |  | No value here. Research shows that film is good for reflecting solar gain but poor at limiting thermal conductivity
Single Glazed Window |  |  | 0.23256 | 4.3
Single Glazed Window with K glass |  |  | 0.40933 | 2.443
Double Glazed with Argon Filling |  |  | 0.38462 | 2.6
Double Glazed with Argon filling and K glass |  |  | 0.5 | 2
Secondary Double Glazed (4mm Hard E Coat glass) |  |  | 0.53533 | 1.868
Wooden Door (Internal) |  |  | 0.27027 | 3.7
Wooden Door (External) |  |  | 0.37453 | 2.67
Cavity_insulation
None |  |  | 0
Air (50 mm) | 0.05 | 0.2778 | 0.17999 | 5.556
Air (100 mm) | 0.1 | 0.2778 | 0.35997 | 2.778
Expanded Polystyrene Slab | 0.1 | 0.035 | 2.8571 | 0.35
Mineral Wool (Batt or Slab) | 0.1 | 0.038 | 2.6316 | 0.38
Phenolic Foam Board | 0.1 | 0.025 | 4 | 0.25
Polyurethane Board | 0.1 | 0.025 | 4 | 0.25
Urea formaldehyde foam (post build installation) | 0.1 | 0.04 | 2.5 | 0.4
Blown in mineral wool* | 0.1 | 0.042 | 2.381 | 0.42
Floor_Type
None |  |  | 0
Concrete (100mm) | 0.1 | 1.33 | 0.075188 | 13.3
Concrete (100mm) over Phenolic Board (100mm) |  |  | 3.3536 | 0.29819
Floor Boards (Softwood 22mm) | 0.022 | 0.13 | 0.16923 | 5.9091
Floor Boads (Hardwood 22mm) | 0.022 | 0.18 | 0.12222 | 8.1818
Floor Boards (Chip board, 19mm) | 0.019 | 0.14 | 0.13571 | 7.3684
Ceiling
None |  |  | 0
Plaster Board (13mm inc skim) | 0.013 | 0.16 | 0.08125 | 12.3077
Plaster Board With (100mm mineral wool and skim) |  |  | 2.8168 | 0.35501
Surface Resistance (Internal) |  |  | 0.123 | 8.1301
Surface Resistance (External) |  |  | 0.08 | 12.5
Slab over Kingspan (100mm) | 0.1 | 0.025 | 4 | 0.25
Notes | conductance (K) is measured in W/mKelvin
resistance 'R' is thickness of material in metres divided by the conductance (L/K)
U' value is 1/R
For layers of different U materials add up the conductance values for each element and then calculate U = 1/ K total not forgetting to add the surface resistance values (see below)
Use Rsi =0.123 and Rse = 0.080 for the internal and external surface resistances respectively or choose the appropriate values for your building from the table below:
Internal surface resistances (Rsi)
| Walls | 0.123
| Floors & Ceilings for upward heat flow | 0.104 |  | from the Building Construction Handbook, 8th Edition, Page 469
| Floors & Ceilings for downward heat flow | 0.148
External surface resistance
| Surface |  | Exposure
|  |  | Sheltered | Normal | Severe
| Wall - High Emissivity |  | 0.08 | 0.055 | 0.03
| Wall - Low Emissivity |  | 0.11 | 0.07 | 0.03
| Roof - High Emissivity |  | 0.07 | 0.045 | 0.02
| Roof - Low Emissivity |  | 0.09 | 0.05 | 0.02
| Floor - High Emissivity |  | 0.07 | 0.04
Sheltered - town buildings to 3 storeys
Normal - town buildings 4 to 8 storeys and most suburban premises
Severe - > 9 storeys in towns, 5 storeys eleswhere and any buildings on exposed coasts or hills

## System volume (UFH)
Pipe internal diameter
12 | mm | 0.00011314
Cicuit Length
72 | metres
54
41
167 | Total length
Circuit Volume
18.8949 | Litres

## Notes
Notes | conductance (K) is measured in W/mKelvin
resistance 'R' is thickness of material in metres divided by the conductance (L/K)
U' value is 1/R
For layers of different U materials add up the conductance values for each element and then calculate U = 1/ K total not forgetting to add the surface resistance values (see below)
Use Rsi =0.123 and Rse = 0.080 for the internal and external surface resistances respectively or choose the appropriate values for your building from the table below:
Internal surface resistances (Rsi)
| Walls | 0.123
| Floors & Ceilings for upward heat flow | 0.104 |  | from the Building Construction Handbook, 8th Edition, Page 469
| Floors & Ceilings for downward heat flow | 0.148
External surface resistance
| Surface |  | Exposure
|  |  | Sheltered | Normal | Severe
| Wall - High Emissivity |  | 0.08 | 0.055 | 0.03
| Wall - Low Emissivity |  | 0.11 | 0.07 | 0.03
| Roof - High Emissivity |  | 0.07 | 0.045 | 0.02
| Roof - Low Emissivity |  | 0.09 | 0.05 | 0.02
| Floor - High Emissivity |  | 0.07 | 0.04
Sheltered - town buildings to 3 storeys
Normal - town buildings 4 to 8 storeys and most suburban premises
Severe - > 9 storeys in towns, 5 storeys eleswhere and any buildings on exposed coasts or hills